## Slide 1
Solar Tank Storage vs Batteries
Notes: This module provides an understanding of how to select and configure a system for specific customer needs using the LORENTZ COMPASS software.
Introduction to COMPASS
Helping yourself
Key terms
COMPASS training
  Screen layout and overview
  Quick sizing
  Pump datasheets and information
  Saving projects and providing pdf outputs

## Slide 2: Two important concepts
Water per day
  Total water requirements for the application
  Pump water during daylight hours
Store water not electricity
  Make water available when needed
  Simple and efficient

## Slide 3: Two important concepts
Water per day
  Historically pumps have been specified based on the flow they deliver per minute or hour. For example 1000 litres per hour or 264 USG per hour or 4.2 gallons per minute
  With solar pumping you are looking to maximise the water pumped while the sun shines. For this reason litres (or cubic metres or gallons) per day is the critical measurement
  Always talk about customer requirements per day rather than per hour to avoid confusion
Store water not electricity
  Relying on batteries to pump water overnight introduces cost and complexity to a solution
  Batteries are heavy, expensive, difficult to transport and dispose of and have a limited (3 year typically) life
  Storing water in an elevated tank is efficient and means water is always available

## Slide 4: Initial Site Information
Borehole Site – Dadaab, Kenya
Borehole Depth – 60m
Borehole Yield – 3 m3/hr
Daily Water Requirement – 10 m3
Avg Daily Solar Irradiation – 6 kWh/m2
Ambient Temp – 30oC

## Slide 5: Average Daily Irradiation (EA)
kWhr/m3

## Slide 6: Case 1: 10m3/day/No Tank
Using Compass Solar Pump Tool
PS600 HR-10 Selected
Avg Daily Output 10m3hr
Solar Power Required: 750Wp (3 Panels of 250W)
Detailed Design Report Attached

## Slide 7: Water Produced/Consumed
Chart: No Storage – What is Produced is Consumed Immediately
| 06:00 | 07:00 | 08:00 | 09:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00
Produced | 0 | 0 | 0.57 | 1.1 | 1.3 | 1.5 | 1.5 | 1.5 | 1.3 | 1 | 0.53 | 0 | 0
Consumed | 0 | 0 | 0.57 | 1.1 | 1.3 | 1.5 | 1.5 | 1.5 | 1.3 | 1 | 0.53 | 0 | 0

## Slide 8: New Site Information
Daily Water Requirement – 16 m3
Avg of 1 m3/hr is required up to 11pm at night.
All other factors remain constant.

## Slide 9: Case 2: 16m3/day (Plus Tank)
Using Compass Solar Pump Tool
Use 10m3 storage tank for night consumption
PS600 HR-10 Selected
Avg Daily Output 16m3hr
Solar Power Required: 1,500Wp (6 Panels of 250W)
Detailed Design Report Attached
Additional CAPEX: 1 No 10m3 tank, 3 No Panels of 250W.
Additional O&M: None.

## Slide 10: Water Produced/Consumed
Chart: 10m3 Storage – 1 m3/hr available from 8am per hr till 11pm
| 06:00 | 07:00 | 08:00 | 09:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
Produced | 0 | 0.48 | 1.5 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.4 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0
Consumed | 0 | 0.48 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.94
Storage Tank | 0 | 0 | 0.5 | 1.3 | 2.1 | 2.9 | 3.7 | 4.5 | 5.3 | 6.1 | 6.5 | 5.94 | 4.94 | 3.94 | 2.94 | 1.94 | 0.94 | 0

## Slide 11: Case 3: 16m3/day (Plus batteries)
Using Compass Solar Pump Tool
PS600 HR-10 Selected
Daily Power Reqts:
  At 48VDC Battery Voltage.
  Power = 392 W, Flow = 1.3m3/hr
  For 16m3/day, pump needs 16/1.3 = 12.3 operating hrs per day.
  392 x 12.3 = 4,822 Wh per day.
  4,822/48 = 100 Ah.
  Battery Depth of discharge 50% -> Use 100Ah/050% = 200 Ah
Battery Array – Use 2 strings of 4 12 V, 100 AH batteries to achieve 48V, 200AH power.

## Slide 12: Case 3: 16m3/day (Plus batteries)
Array Sizing:
  Battery efficiency 85%
  Wiring efficiency 97%
  PV efficiency: 90% (cell temp/dirt)
  PV battery mismatch (MPPT tracking) 100%
  PV Charge controller efficiency: 95%
  Total Efficiency factor
  .85*.97*.9*1*.95 = 0.70
Solar Array Size = 4,822Wh/6kWh = 804 Wp Solar Array / 0.7 losses = 1,149 Wp
6 SOLAR PANELS OF 250 Wp
Additional CAPEX: 8 No 100Ah batteries, 30A Charge Controller, 3 No Panels of 250W.
Additional O&M: Battery Replacement every 3-5 years.

## Slide 13: Water Produced/Consumed
Chart: Battery Backup
| 06:00 | 07:00 | 08:00 | 09:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
Produced | 0 | 0 | 0 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 0 | 0 | 0
Consumed | 0 | 0 | 0 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 0 | 0 | 0

## Slide 14: Comparison
 | Case 1 | Case 2 | Case 3
Flow | 10m3/day | 16m3/day | 16m3/day
Pump | PS600 HR-10 | PS600 HR-10 | PS600 HR-10
# Panels | 3 x 250 Watts | 6 x 250 Watts | 6 x 250 Watts
Tank | 0 | 1 No 10,000 lit (Budget K 80,000) | 0
Batteries | 0 | 0 | 8 No 12 V, 100 AH (Budget K 180,000)
Other Accessories |  | Float Switch | Charge Controller (Budget 30,000)
Supply Period | 8:00 – 16:00 | 8:00 – 23:00 | 8:00 – 20:00
O&M | None | None | Batteries (3 - 5yrs)

## Slide 15
THANK YOU!
Q&A